## Branding (hidden)
SUVI CHEM™ CONSULTANCY SERVICES
Heat Exchanger Diagnostic Toolkit — Bell–Delaware Method | Version 1.0
© SUVI CHEM Consultancy Services ¦ Proprietary Engineering Toolkit
Licensed Copy — Not for Redistribution
© SUVI CHEM™ Consultancy Services

## Home_Dashboard
SUVI CHEM™ CONSULTANCY SERVICES
Heat Exchanger Diagnostic Application
| THERMAL STATUS |  |  | HYDRAULIC STATUS
|  | OK |  |  | EXCEEDS LIMIT
OVERALL VERDICT
| Why | Shell-side pressure drop exceeds allowable limit
| U dirty (W/m²·K) |  | 61.3744 |  |  | Tube ΔP (bar)
0.0059161
| Required Area (m²) |  | 79.03
Governing Allowable: 0.100 bar
| Installed Area (m²) |  | 250 |  |  | Shell ΔP (bar)
5.4374
| LMTD Status |  | ✅ LMTD OK
Governing Allowable: 1.00 bar
Disclaimer
SUVI CHEM™ HX Diagnostic Toolkit ¦ Bell–Delaware Method Version 1.0
Input Form
ΔP Details
View Results
Recommendations
Disclaimer
Note on H26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allowable ΔP Logic: • If client/process datasheet specifies allowable ΔP, that value governs. • If no datasheet value is provided, an industry guideline ΔP based on fluid type is used. • Exceeding allowable ΔP indicates potential operability or pumping limitations and requires engineering review.

## Input_Form
PROCESS INPUT FORM
Enter operating and design data below
TUBE SIDE INPUTS
Fluid | Propylene Glycol
Tube Inside Diameter | 0.75 | inch | 0.01905 | Mass flow rate | 20000 | kg/h | 5.5556
Tube Length | 5 | m | 5 | Density | 1035 | kg/m³ | 1035
Number of tubes | 100 | Nos |  | Viscosity | 0.042 | Pa·s | 0.042
Number of Passes | 2 | Nos |  | Specific heat | 2400 | J/kg·K | 2400
Installed Heat Transfer Area (Vendor / Datasheet) | 250 | m² | 250 | Thermal conductivity | 0.21 | W/m·K | 0.21
Temperature Correction | Yes
1
SHELL SIDE INPUTS
Fluid | Water
Shell inside diameter | 600 | mm | 0.6 | Shell mass flow | 20000 | kg/h | 5.5556
Tube outside diameter | 25 | mm | 0.025 | Density | 998 | kg/m³ | 998
Tube pitch | 32 | mm | 0.032 | Viscosity | 0.001 | Pa·s | 0.001
Baffle spacing | 350 | mm | 0.35 | Specific heat | 4180 | J/kg·K | 4180
Tube Layout | Triangular |  |  | Thermal conductivity | 0.6 | W/m·K | 0.6
Layout Angle | 30° / 60°
Baffle Cut | 30 | %
Shell-Baffle Clearance | 3 | mm |  | Inlet Baffle Spacing (Lb_in) | 350 | mm
Tube-Baffle Clearance | 0.4 | mm |  | Outlet Baffle Spacing (Lb_out) | 350 | mm
Pitch ratio Pt/Do | 1.28 | ✅ Pt/Do OK
Tube Bundle OD Db |  | mm
Tube Bundle OD is estimated from tube count and tube pitch if OD is not provided.
PROCESS TEMPERATURES
Tube-side Inlet Temperature | 90 | °C
Tube-side Outlet Temperature | 70 | °C
Shell-side Inlet Temperature | 85 | °C
Shell-side Outlet Temperature | 75 | °C
FOULING & ALLOWABLES
Tube-side Fouling Resistance | 0.001 | m²·K/W |  | Allowable Tube-side ΔP | 10000 | Pa | 10000
Shell-side Fouling Resistance | 0.00012 | m²·K/W |  | Allowable Shell-side ΔP | 10000 | Pa | 10000
|  |  |  | Guideline allowable Shell side ΔP | 50 | KPa | 50000
|  |  |  | Guideline allowable Tube side ΔP | 220 | KPa | 220000

## Results_Dashboard
RESULTS DASHBOARD
Thermal and hydraulic performance summary
THERMAL PERFORMANCE |  |  |  |  | HYDRAULIC PERFORMANCE
Overall Heat Transfer Coefficient (Dirty) | 61.3744 | 61.3744 | W/m²·K | 61.3744 | Tube-side Pressure Drop | 591.6075 | 0.0059161 | bar | 0.0059161
Required Heat Transfer Area | 79.03 | 79.03 | m² | 79.03 | Allowable Tube-side ΔP | 10000 | 0.1 | bar | 0.1
Installed Heat Transfer Area (Vendor / Datasheet) | 250 | 250 | m² | 250 | Shell-side Pressure Drop | 543743.8815 | 5.4374 | bar | 5.4374
Area Margin | 216.3355 | 216.3355 | % |  | Allowable Shell-side ΔP | 10000 | 0.1 | bar | 0.1
Capacity Utilization |  | 31.612 | % |  | Governing side |  | Shell-side
Thermal Status | OK | OK |  |  | Hydraulic Status | ⚠ CHECK ΔP | ⚠ CHECK ΔP
DIAGNOSTIC INSIGHT
HYDRAULICALLY CONSTRAINED: Pressure drop exceeds allowable limits.
Unit consistency check: PASSED.

## Recommendations
RECOMMENDATIONS
SHORT TERM - ⚙ OPERATIONAL
• Reduce shell-side flow rate. •Redistribute duty among parallel exchangers. •Review operating temperature to reduce viscosity if process permits.
• Maintain clean shell-side conditions to prevent fouling that further reduces effective hydraulic diameter.
• Monitor vibration and consider partial bypassing if shell-side ΔP limits operation.
MEDIUM TERM -🛠 MAINTENANCE
• Inspect exchanger internals for fouling, blockage, or damaged baffles reducing effective flow area during next shutdown.
• Repair or replace damaged baffles causing excessive leakage.
• Install sealing strips or correct bundle positioning during maintenance to reduce shell-to-bundle bypass flow.
LONG TERM - 🏗 REVAMP
• Reduce shell-side mass velocity by increasing baffle spacing or shell diameter
• Increase cross-flow area by increasing baffle spacing or shell diameter
• Consider increasing tube pitch to improve hydraulic diameter
• Reduce number of baffles by increasing baffle spacing
• Review shell-to-baffle and tube-to-baffle clearances to reduce leakage
• Provide sealing strips to reduce shell-to-bundle bypass flow

## ΔP Details
ΔP SUMMARY
Parameter |  |  | UoM |  | Tube Side |  | Shell Side
Calculated ΔP |  |  | Pa |  | 591.6075 |  | 543743.8815
Governing Allowable ΔP |  |  | Pa |  | 10000 |  | 10000
Margin |  |  | Pa |  | 9408.3925 |  | -533743.8815
Status |  |  | - |  | OK |  | FAIL
Governing Basis
Tube side Allowable ΔP |  |  | Governing basis: Process datasheet (client-specified limit)
Shell side Allowable ΔP |  |  | Governing basis: Process datasheet (client-specified limit)
Shell-Side ΔP Diagnostic Table
Parameter |  | UoM | Calculated Value | Recommended Range | Status | Engineering Remark
Mass velocity (Gₛ) |  | kg/m²·s | 120.9373 | ≤ 100 | REVIEW | High shell-side velocity increasing ΔP
Cross-flow area (Aₛ) |  | m2 | 0.045937 | ≥ 0.06 | REVIEW | Limited area causing high velocity
Equivalent diameter (Dₑ) |  | m | 0.027095 | ≥ 0.03 | REVIEW | Small hydraulic diameter
No. of cross-flow sections (N_cf) |  | - | 12 | ≤ 8 | REVIEW | Excessive baffles increasing ΔP
Leakage factor (Rₗ) |  | - | 0.77517 | ≥ 0.85 | REVIEW | High baffle/tube leakage
Bypass factor (R_b) |  | - | 0.60927 | ≥ 0.70 | REVIEW | Strong bundle bypass
Theoretical shell ΔP |  | Bar | 11.5131 | — | Reference | ΔP without leakage/bypass
Actual shell-side ΔP |  | Bar | 5.4374 | 1 | FAIL | Exceeds allowable shell-side ΔP
Parameter Violation Summary
• High shell-side mass velocity
• Limited cross-flow area
• Small equivalent diameter
• Excessive number of baffles
• High baffle / tube leakage
• Significant bundle bypass
Hydraulic concerns identified |  |  | 7
Note on B19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shell-side mass velocity (Gs) governs frictional pressure drop. ΔPcf ∝ Gs² / (2ρ) High Gs significantly increases shell-side pressure drop and vibration risk. Reference: Bell & Mueller (1973), AIChE Symposium Series Kern, Process Heat Transfer
Note on B20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cross-flow area (As) is the effective flow area normal to shell-side cross-flow. Gs = ṁ / As Low As increases velocity and pressure drop. Reference: Bell–Delaware Method Perry’s Chemical Engineers’ Handbook
Note on B21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Equivalent diameter (De) represents hydraulic diameter for shell-side cross-flow. Smaller De increases friction factor and pressure drop. De depends on tube layout and pitch. Reference: Bell–Delaware correlations Perry’s Chemical Engineers’ Handbook
Note on B22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Number of cross-flow sections (N_cf) represents the number of times shell-side fluid crosses the tube bundle. N_cf = L_s / L_b Shell-side pressure drop increases approximately linearly with N_cf. Excessive N_cf indicates tight baffle spacing, which increases hydraulic resistance. Reference: Bell & Mueller (1973), AIChE Symposium Series Bell–Delaware Method Perry’s Chemical Engineers’ Handbook
Note on B23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leakage correction factor (Rl) accounts for shell-to-baffle and tube-to-baffle leakage. Rl < 1 indicates flow leakage reducing effective cross-flow. Typical values: 0.85–0.95 Reference: Bell & Mueller (1973) University of Delaware Heat Exchanger Program
Note on B24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bypass correction factor (Rb) accounts for shell-to-bundle bypass flow. Low Rb indicates significant bypassing, reducing heat transfer effectiveness. Typical values: 0.70–0.90 Reference: Bell–Delaware Method TEMA mechanical tolerances

## Legal_Disclaimer
ENGINEERING DISCLAIMER, NO LIABILITY & TERMS OF USE
ENGINEERING DISCLAIMER
This Heat Exchanger Diagnostic Toolkit is intended for preliminary engineering analysis, performance evaluation, troubleshooting, and training purposes only based mainly on Bell-Delaware method. The calculations are based on standard chemical engineering correlations and user-provided inputs. This toolkit does not replace detailed design using licensed commercial software, statutory code compliance checks, or approval by competent authorities. All results must be independently reviewed and validated by qualified engineers before implementation.
NO LIABILITY CLAUSE
SUVI CHEM Consultancy Services shall not be liable for any direct or indirect losses, including but not limited to production loss, equipment damage, safety incidents, financial loss, or regulatory non-compliance arising from the use or misuse of this toolkit. The user assumes full responsibility for decisions taken based on the outputs of this toolkit.
TERMS OF USE
This toolkit is licensed for single-user or single-organization internal use only. Redistribution, resale, sublicensing, or sharing of this file or its contents is strictly prohibited. All formulas, structure, and methodology remain the intellectual property of SUVI CHEM Consultancy Services. Use of this toolkit constitutes acceptance of these terms. Governing law: India. Jurisdiction: Maharashtra.
Physical properties are typical reference values at near-ambient conditions. Actual properties vary with temperature, pressure, and composition. Users must verify properties for final design and safety decisions.
⚠ This workbook is protected. Unauthorized modification, reverse engineering, or redistribution is prohibited.

## Unit_Check (hidden)
Tube side Flow–Cp unit consistency | OK
Value not available | OK
Value not available | OK
Shell Flow–Cp unit consistency | OK
Tube side Pressure unit & ΔP base consistency | OK
Shell side Pressure unit & ΔP base consistency | OK
Fouling Resistance and Unit validity | OK
OK

## Unit_Control (hidden)
Length |  |  | Pressure |  | Flow |  | Area |  | Viscosity |  | Density |  | Specific Heat Cp |  | Thermal Conductivity |  | Heat Transfer Coefficient
Unit | to_m |  | Unit | to_Pa | Unit | to_kg_s | Unit | To_m2 | Unit | To_Pa_s | Unit | To_kg_m3 | Unit | To_J_kgK | Unit | To_W_mK | Unit | To_W_m2K
m | 1 |  | Pa | 1 | kg/s | 1 | m² | 1 | Pa·s | 1 | kg/m³ | 1 | J/kg·K | 1 | W/m·K | 1 | W/m²·K | 1
mm | 0.001 |  | kPa | 1000 | kg/h | 0.00027778 | ft² | 0.092903 | cP | 0.001 | g/cm³ | 1000 | kJ/kg·K | 1000 | W/m·°C | 1 | W/m²·°C | 1
inch | 0.0254 |  | bar | 100000 | lb/h | 0.000126 | [6 empty] | cal/g·°C | 4186 | kcal/m·h·°C | 1.163 | kcal/m²·h·°C | 1.163
ft | 0.3048 |  | psi | 6894.76 | [8 empty] | kcal/kg·°C | 4186 | kcal/m·h·K | 1.163 | kcal/m²·h·K | 1.163
[13 empty] | Btu/lb·°F | 4186.8 | Btu/h·ft·°F | 1.7307 | Btu/h·ft²·°F | 5.678
|  |  | Unit | Factor from Pa
|  |  | Pa | 1
|  |  | kPa | 0.001
|  |  | bar | 1e-05
|  |  | psi | 0.00014504
TEMPERATURE HELPERS
| Parameter | Formula | Result
| Tube-side Mean Temperature | 80 | °C
| Shell-side Mean Temperature | 80 | °C
| Tube-side evaluation temperature | 80 | °C
| Shell-side evaluation temperature | 80 | °C

## Tube_Inputs (hidden)
Parameter | Symbol | Value | Units
Tube inside diameter | Di | 0.01905 | m
Tube length | L | 5 | m
Number of tubes | Nt | 100 | -
Number of passes | Np | 2 | -
Mass flow rate | m_dot | 5.5556 | kg/S
Density | rho | 1003.6912 | kg/m3
Viscosity | mu | 0.0046822 | Pa.s
Specific heat | Cp | 2433 | J/kg.K
Thermal conductivity | k | 0.20769 | W/m.K

## Shell_Inputs (hidden)
Parameter | Symbol | Value | Units
Shell inside diameter | Ds | 0.6 | m
Tube outside diameter | Do | 0.025 | m
Tube pitch | Pt | 0.032 | m
Baffle spacing | Lb | 0.35 | m
Shell mass flow | m_s | 5.5556 | kg/s
Density | rho_s | 981.533 | kg/m3
Viscosity | mu_s | 0.00053428 | Pa.s
Specific heat | Cp_s | 4202.99 | J/kg.K
Thermal conductivity | k_s | 0.5934 | W/m.K
jH factor | jH | 0.00096252 | -
Jc | Jc | 0.766 | -
Jl | Jl | 0.77517 | -
Jb | Jb | 0.7 | -
Js | Js | 1 | -
Jr | Jr | 1 | -

## Shell_DP (hidden)
Calculation | Value (Pa) | Formula
Mass flow (kg/s) | 5.5556 | ṁ = m_s / 3600 | [5 empty] | ROOT-CAUSE DETECTION
Cross-flow area As | 0.045937 | As = Ds·(Pt−Do)/Pt·Lb
Mass velocity Gs | 120.9373 | Gs = ṁ / As |  |  |  |  | Gs | OK | Shell mass velocity is high | → Reduce shell flow rate | → Increase baffle spacing | → Increase shell diameter
Equivalent diameter De | 0.027095 | Bell–Delaware De |  |  |  |  | Lb/Ds | OK | Baffle spacing too small | → Increase Lb to 0.4–0.6 Ds | → Reduces N_cf and ΔP
ΔP per cross-flow section | 1.7598 | ΔP = f·(Gs²/2ρ)·(Lb/De) |  |  |  |  | Ncf | HIGH_Ncf | Too many cross-flow sections | → Increase baffle spacing | → Reduce shell length | → Consider two shells in parallel
Number of baffles (Nb) | 13 | [5 empty] | Pt/Do | OK | Tight tube pitch increases resistance | → Increase Pt/Do to 1.33 or 1.5 | → Reduces ΔP significantly
Total Shell-side ΔP | 543743.8815 | Pa |  |  |  |  | Bypass Fraction | HIGH_BYPASS | High bundle bypass | → Add sealing strips | → Reduce shell–bundle clearance
| 5.4374 | Bar
[8 empty] | Action | ΔP Impact
[8 empty] | Reduce Gs | 🔥🔥🔥🔥
IDEAL CROSS-FLOW PRESSURE DROP (ΔP_cf) | [7 empty] | Increase Lb | 🔥🔥🔥
C factor | 2.5 | (triangular & square – acceptable for rating) | [5 empty] | Increase Pt/Do | 🔥🔥
Friction factor for shell-side cross-flow fs | 0.67575 | [6 empty] | Add sealing strips | 🔥
Pressure drop per cross-flow section (ΔP_cf1) | 63961.4962 | fs * (Gs^2/(2*rho_s)) * (Lb/de)
IDEAL CROSS-FLOW PRESSURE DROP (ΔP_cf) | 767537.9546 | [5 empty] | Parameter | Screening Range | Reference Basis | Literature support
Number of cross-flow sections (N_cf) | 12 | [5 empty] | Gₛ | ≤ 100 kg/m²·s | Bell–Delaware ΔP sensitivity, Kern | Kern (Process Heat Transfer): | “Shell-side velocities are generally kept lower than tube-side velocities to limit pressure drop and vibration.” | Perry’s Handbook: | Typical shell-side mass velocities correspond to 0.5–2 m/s, which maps to ~50–100 kg/m²·s for liquids. | “Recommended shell-side mass velocity based on Bell–Delaware pressure-drop sensitivity and standard exchanger practice.”
[6 empty] | 1151306.9319 | Aₛ | Velocity-based | Bell–Delaware flow area definition | Bell & Mueller (1973): | Cross-flow area reduction significantly increases ΔP_cf. |  |  | “Cross-flow area assessed relative to shell-side mass velocity; low effective area contributes to elevated pressure drop.”
WINDOW ZONE PRESSURE DROP (ΔP_w) | 383768.9773 |  |  |  |  | 607563.0504 | Dₑ | ≥ 0.03 m | Perry, Bell–Delaware friction | Perry’s Handbook: | Smaller hydraulic diameters increase friction losses sharply. | Bell–Delaware reports sensitivity of ΔP to tube pitch & layout via Dₑ. |  | “Equivalent diameter evaluated as a hydraulic indicator; low Dₑ increases frictional pressure drop per Bell–Delaware correlations.”
[7 empty] | Rₗ | ≥ 0.85 | Bell–Delaware leakage factor | Bell & Mueller (1973), Fig. correlations: | Typical industrial exchangers: Rₗ ≈ 0.85–0.95 | Poor mechanical condition: Rₗ < 0.8 |  | “Leakage correction factor evaluated per Bell–Delaware method; values below 0.85 indicate significant leakage paths.”
Leakage correction on ΔP--Rl | 0.77517 | [5 empty] | R_b | ≥ 0.70 | Bell–Delaware bypass factor | Bell–Delaware studies show: | R_b ≈ 0.7–0.9 → typical designs | R_b < 0.7 → severe bypass | TEMA tolerances without sealing strips commonly lead to R_b ≈ 0.6–0.7 | “Bypass correction factor per Bell–Delaware methodology; values below 0.70 indicate strong bundle bypass and reduced exchanger effectiveness.”
Bundle bypass correction on ΔP--Rb | 0.60927 | [6 empty] | These are not hard “code limits”. They are widely used screening / diagnostic ranges derived from Bell–Delaware practice, HTRI-style guidance, and exchanger design texts.
Ideal Delta P | 1151306.9319 | Pa
| 11.5131 | Bar
|  |  | WHY DATASHEET ΔP OVERRIDES GUIDELINES |  |  |  |  | What datasheet allowable ΔP represents
Label | Value |  | What guideline limits are | [5 empty] | Pump/compressor capability
ΔP_low_limit | 50000 | Pa |  |  | Typical / empirical limits |  |  |  | System hydraulics
ΔP_high_limit based on fluid | 50000 | Pa |  |  | Based on experience, not process necessity |  |  |  | Control valve margin
ΔP_critical | 150000 | Pa |  |  | Used when no constraint is provided |  |  |  | Operability constraints
|  |  |  | Examples: | Cooling water: 50–70 kPa |  |  |  | Energy cost limits
Total Shell-side ΔP based on general guidelines | ❌ CRITICAL |  |  |  | Hydrocarbon liquid: 70–100 kPa |  |  |  | 👉 It is a hard process constraint, not a suggestion.
[5 empty] | Gas: 10–40 kPa |  |  |  |  | Ignoring it can cause:
|  |  |  | These are engineering defaults, not requirements. | [5 empty] | Pump overload
Governing allowable ΔP | 10000 | Pa | [7 empty] | Loss of turndown
| 1 | Bar | [7 empty] | Control issues
|  | Where specified, client/process datasheet allowable ΔP governs acceptance. | [7 empty] | Contractual non-compliance
Guideline limits are applied only when no datasheet value is provided.
ΔP Reduction Guidance | Reduce Gs
Increase Lb
Increase Pt/Do
Add sealing strips
Core sources (industry-accepted)
1. Bell, K.J. & Mueller, A.C.
“Flow Distribution and Heat Transfer in Shell-and-Tube Heat Exchangers”
AIChE Symposium Series, Vol. 69, No. 131, 1973
2. Bell, K.J.
“Final Report of the Cooperative Research Program on Shell-and-Tube Heat Exchangers”
University of Delaware, 1963–1970
3. Kern, D.Q.
Process Heat Transfer, McGraw-Hill
4. Perry & Green
Perry’s Chemical Engineers’ Handbook, Heat Transfer Section
5. TEMA Standards
(for mechanical clearances, baffle practice, not direct ΔP limits)

## Tube_DP (hidden)
Calculation | Value (Pa) | Formula
Friction factor (f) | 0.059547 | f = 0.316/Re^0.25 (Blasius)
ΔP per pass | 295.8037 | ΔP = f·(L/Di)·(ρ·v²/2)
Total Tube-side ΔP | 591.6075 | ΔPt = ΔP/pass × No. of passes
Allowable Delta P as per Client input | 10000 | Pa
Guided line Allowable Delta P as per Fluid | 220000 | Pa
Governing allowable ΔP | 10000 | Pa

## DP_Checks (hidden)
ΔP CHECKS & WARNINGS
Parameter | Value (Pa) | Allowable (Pa) | Status
Tube-side ΔP | 591.6075 | 10000 | OK
Shell-side ΔP | 543743.8815 | 10000 | EXCEEDS LIMIT

## Shell_HT (hidden)
Calculation | Value | Formula (Reference) |  | Bell–Delaware ideal j-factor constants
Mass flow (kg/s) | 5.5556 | ṁ = m_s / 3600 |  | Layout | Pt/Do | a | b
Cross-flow area As (m2) | 0.045937 | As = Ds·(Pt−Do)/Pt·Lb |  | Triangular | 1.25 | 0.2 | 0.6
Mass velocity Gs (kg/m2.s) | 120.9373 | Gs = ṁ / As |  | Triangular | 1.33 | 0.18 | 0.62
Equivalent diameter De (m) | 0.027095 | De = 1.27·(Pt² − 0.785·Do²)/Do |  | Triangular | 1.5 | 0.15 | 0.65
Reynolds Res | 6133.1757 | Re_s = Gs·De / μ |  | Square | 1.25 | 0.16 | 0.62
Prandtl Prs | 3.7843 | Pr_s = Cp·μ / k |  | Square | 1.33 | 0.14 | 0.65
h_ideal (W/m2.K) | 201.4694 | h_ideal = jH·Gs·Cp / Pr^(2/3) |  | Square | 1.5 | 0.12 | 0.68
hs (W/m2.K) | 83.7395 | hs = h_ideal·Jc·Jl·Jb·Js·Jr
|  |  |  | Interpolation of a and b based on calculated Pt/Do |  |  | a1 | b1
Ideal Shell-Side Heat-Transfer j-Factor (jₕ) |  |  |  | Lower bounding Pt/Do |  | 1.25 | 0.2 | 0.6
jh | 0.00096252 |  |  | Upper bounding Pt/Do |  | 1.33 | 0.18 | 0.62
⚠ jₕ outside typical Bell range
|  |  |  | Interpolated a |  | 0.1925
Jc : Baffle Cut & Spacing Correction |  |  |  | Interpolated b |  | 0.6075
Baffle spacing ratio (Lb/Ds) | 0.58333 | Typical range: 0.2 – 1.0
Baffle cut fraction | 0.3
Jc | 0.766
Final Jc | 0.766 | Jc never > 1.0, Jc never unrealistically low
✅ Baffle cut typical
Jl : Leakage Correction Factor
Shell-to-baffle leakage area (Asb) | 5654.8668 | mm2
Tube-to-baffle leakage area (Atb) | 3141.5927 | mm2
Total leakage area (Al) | 8796.4594 | mm2
EFFECTIVE CROSS-FLOW AREA (Ac) | 45937.5 | mm2
Leakage Area Ratio | 0.19149 | Typical values: Typical values: 0.01 – 0.15 → normal, > 0.25 → excessive leakage
JL | 0.77517
Final Jl | 0.77517
✅ Leakage within typical range
Jb: Bundle Bypass Correction
Bundle bypass gap (radial) | 128.462 | mm
Bypass area fraction (simplified) | 0.36703
Jb_raw | 0.60927
Final Jb | 0.7
❌ Severe bundle bypass – sealing strips recommended
Tube Bundle OD (Db) (ENGINEERING METHOD) | tube-count-based approximation
Layout constant K | 0.87
Estimated Db (from tube count) | 343.076 | mm | Estimated from tube count and pitch. Use for rating only.
Final Db used in calculations | 343.076
⚠ Db estimated from tube count
Compare Db vs Shell ID. | ✅ Db/Shell ID reasonable
Typical:
Db/Ds ≈ 0.85 – 0.95
Js: Unequal Baffle Spacing Correction
Js raw | 1 | In case Inlet and outlet baffle spacings were not available; therefore, equal spacing was assumed and no Js correction was applied.
Inlet spacing ratio | 1
Outlet spacing ratio | 1
✅ Baffle spacing acceptable
Jr Laminar flow correction
Jr_raw | 1
✅ Turbulent flow – no Jr correction
FINAL Jr USED IN CALCULATION | 1

## Tube_HT (hidden)
Calculation | Value | Formula (Reference)
Mass flow (kg/s) | 5.5556 | ṁ = m_dot
Flow area (m2) | 0.028502 | A = Nt·π·Di² / 4
Velocity (m/s) | 0.1942 | v = ṁ / (ρ·A)
Reynolds | 793.0389 | Re = ρ·v·Di / μ
Prandtl | 54.8498 | Pr = Cp·μ / k
Nusselt | 23.8141 | Nu = 0.023·Re^0.8·Pr^0.4
hi (W/m2.K) | 259.6294 | hi = Nu·k / Di

## Overall_Rating (hidden)
Calculation | Value | Formula (Reference)
U dirty (W/m2.K) | 61.3744 | Udirty = 1 / (1/hi + 1/hs + Rfi + Rfo)
Required Area (m2) | 79.03 | Areq = Q / (Udirty·LMTD·Ft) | Heat duty converted from kJ/h to W for area calculation.
Installed Area (m2) | 250
Margin (%) | 216.3355 | Margin = (Ainst − Areq) / Areq
Result | OK | PASS if Margin ≥ 0
OK
ΔP Status | ⚠ CHECK ΔP |  | IF( B5="","", IF(B5>=15,"OK", "Insufficient Area"))
EXCEEDS LIMIT
LMTD Correction Factor Ft | 1

## Energy_Check (hidden)
Flow Arrangement | Counter-current
Tube-side Heat Duty (Qₜ) | -270333.3333 | kJ/h
Shell-side Heat Duty (Qₛ) | 233499.4444 | kJ/h
Heat Duty Mismatch | 2 | %
Energy Balance Status | ❌ Check Data
Qavg | 251916.3889 | kJ/h | “Heat duty used for sizing and rating is taken as the average of tube-side and shell-side duties to minimize measurement bias and uncertainty.”
Determine Hot Side | Tube
ΔT1 | 20 | °C
ΔT2 | 10 | °C
LMTD | 14.427 | °C
HEAT DUTY FROM LMTD using U dirty | 221361.3684 | kJ/h
LMTD WARNING STATUS | ✅ LMTD OK

## Chemical_Properties (hidden)
Chemical Name | Density (kg/m3) | Viscosity (Pa.s) | Cp (J/kg.K) | Thermal Conductivity (W/m.K) | Beta (1/C) | C_visc | a_Cp (1/C) | b_k (1/C) | Category | Shell side Allowable ΔP (kPa) | Engineering Basis | Tube-Side Allowable ΔP (kPa) | Engineering Rationale
Water | 998 | 0.001 | 4180 | 0.6 | 0.0003 | 1200 | 0.0001 | 0.0002 | Utility | 50 | Pumping cost & erosion control | 100 | Standard cooling/process water
Methanol | 792 | 0.00059 | 2530 | 0.2 | 0.0011 | 1600 | 0.0004 | 0.0003 | Alcohol | 80 | Light organic liquid | 150 | Low viscosity, easy pumping
Ethanol | 789 | 0.0012 | 2440 | 0.17 | 0.00108 | 1700 | 0.0004 | 0.0003 | Alcohol | 80 | Light organic liquid | 150 | Similar to methanol
Isopropanol | 785 | 0.0024 | 2600 | 0.16 | 0.00105 | 1800 | 0.00045 | 0.00035 | Alcohol | 90 | Slightly more viscous | 150 | Slightly higher viscosity
Acetone | 784 | 0.00032 | 2150 | 0.18 | 0.0013 | 1400 | 0.00035 | 0.0004 | Solvent | 80 | Low viscosity solvent | 150 | Low viscosity solvent
Toluene | 867 | 0.00059 | 1700 | 0.13 | 0.00095 | 1800 | 0.0003 | 0.00025 | Aromatic HC | 100 | Moderate density | 180 | Hydrocarbon, low fouling
Benzene | 876 | 0.00065 | 1740 | 0.15 | 0.001 | 1700 | 0.0003 | 0.00025 | Aromatic HC | 100 | Similar to toluene | 180 | Similar to toluene
Xylene (mixed) | 860 | 0.00073 | 1700 | 0.14 | 0.0009 | 1900 | 0.0003 | 0.00025 | Aromatic HC | 120 | Higher viscosity | 200 | Higher viscosity hydrocarbon
Sulfuric Acid 98% | 1840 | 0.024 | 1380 | 0.5 | 0.0005 | 3500 | 0.0002 | 0.0003 | Acid | 60 | Very high density | 80 | Corrosive, erosion risk
Sulfuric Acid 50% | 1400 | 0.007 | 2900 | 0.43 | 0.00055 | 2800 | 0.00025 | 0.0003 | Acid | 80 | Corrosion / pumping | 100 | Less viscous than 98%
Hydrochloric Acid 30% | 1150 | 0.0019 | 3200 | 0.45 | 0.00045 | 2000 | 0.0002 | 0.00025 | Acid | 70 | Corrosion constraint | 70 | Highly corrosive
Nitric Acid 68% | 1510 | 0.0012 | 1800 | 0.45 | 0.00055 | 2200 | 0.0002 | 0.00025 | Acid | 60 | Oxidizing, corrosion | 80 | Corrosive oxidizer
Sodium Hydroxide 50% | 1520 | 0.005 | 3300 | 0.45 | 0.0004 | 3000 | 0.00025 | 0.00025 | Alkali | 80 | High viscosity | 120 | High viscosity, fouling
Ethylene Glycol | 1110 | 0.016 | 2400 | 0.25 | 0.0006 | 3500 | 0.00025 | 0.0002 | Glycol | 120 | High viscosity | 200 | High viscosity
Propylene Glycol | 1035 | 0.042 | 2400 | 0.21 | 0.00055 | 4200 | 0.00025 | 0.0002 | Glycol | 150 | Very viscous | 220 | Higher viscosity than EG
EG-Water 50% | 1070 | 0.005 | 3300 | 0.39 | 0.00045 | 2600 | 0.0002 | 0.0002 | Glycol mix | 100 | Intermediate viscosity | 180 | Intermediate viscosity
Diesel (typical) | 830 | 0.003 | 2100 | 0.13 | 0.0008 | 2500 | 0.00025 | 0.0002 | Heavy HC | 150 | High viscosity | 250 | High allowable, pumpable
Kerosene | 800 | 0.002 | 2100 | 0.14 | 0.00085 | 2200 | 0.00025 | 0.0002 | Medium HC | 120 | Typical refinery service | 220 | Light hydrocarbon
Cooling Water | 998 | 0.001 | 4180 | 0.6 | 0.0003 | 1200 | 0.0001 | 0.0002 | Utility | 50 | Industry standard | 120 | Often slightly higher than process water
Air | 1.2 | 1.8e-05 | 1005 | 0.026 | 0.0034 | 800 | 0.0001 | 0.0001 | Gas | 20 | Fan/compressor limitation | 30 | Compressibility limits
Boiler Feed Water | 995 | 0.0008 | 4200 | 0.61 | 0.00035 | 1100 | 0.0001 | 0.00025 | Utility | 40 | High purity, cavitation risk | 80 | Pump protection, erosion
Chilled Water (5 °C) | 1000 | 0.0015 | 4180 | 0.58 | 0.00025 | 1300 | 0.0001 | 0.00015 | Utility | 60 | Higher viscosity | 100 | Density higher, pump sensitive
Hot Water (80 °C) | 972 | 0.00036 | 4190 | 0.67 | 0.00035 | 1100 | 0.0001 | 0.00025 | Utility | 70 | Lower viscosity | 120 | Lower viscosity
Steam (sat @ 1 bar) | 0.6 | 1.3e-05 | 2010 | 0.025 | 0.003 | 800 | 0.0005 | 0.0003 | Utility | 20 | Condensing pressure control | 15 | Very sensitive to ΔP | Steam is a gas — HX correlations differ from liquids. These values are for preliminary checks only.
Nitrogen | 1.18 | 1.76e-05 | 1040 | 0.026 | 0.0034 | 800 | 0.0005 | 0.0003 | Gas | 30 | Typical gas-side limit | 25 | Gas compression penalty
[10 empty] | Important Engineering Notes for allowable DeltaP |  | “Tube-side allowable pressure drops are guideline values for preliminary rating.
[10 empty] | Values are guideline only, for continuous operation |  | Final design shall comply with client datasheet or project hydraulic constraints.”
Not valid for:
Two-phase flow
Fouling-dominated services
Transient / batch operation
Final acceptance must satisfy:
Process datasheet
Pump/compressor capability

## Reference for Properties (hidden)
REFERENCES FOR TEMPERATURE CORRELATIONS & CONSTANTS
1️⃣ Density – Linear Thermal Expansion (β)
Correlation used
ρ(T)=ρref [1−β(T−Tref)]\rho(T) = \rho_{ref}\,[1 - \beta (T - T_{ref})]ρ(T)=ρref​[1−β(T−Tref​)]
References
1. Perry & Green – Chemical Engineers’ Handbook, 8th Ed.
Section: Physical Properties of Liquids
States linear thermal expansion is valid for small ΔT
2. Coulson & Richardson – Chemical Engineering, Vol 1
Chapter: Fluid Properties
Typical β ranges:
Water: 0.0002–0.0004 /°C
Organics: 0.0008–0.0013 /°C
3. Incropera & DeWitt – Fundamentals of Heat and Mass Transfer
Density variation approximated linearly for liquids
Why your β values are valid
You used mid-range handbook values
Conservative (do not exaggerate density change)
Standard practice in preliminary design
2️⃣ Viscosity – Andrade / Arrhenius-Type Equation
Correlation used
μ=μref exp⁡ ⁣[C(1T−1Tref)]\mu = \mu_{ref}\,\exp\!\left[C\left(\frac{1}{T}-\frac{1}{T_{ref}}\right)\right]μ=μref​exp[C(T1​−Tref​1​)]
References
1. Reid, Prausnitz & Poling – The Properties of Gases and Liquids, 5th Ed.
Chapter 9: Liquid Viscosity
Andrade-type exponential form recommended
2. Perry’s Handbook, Viscosity section
Simplified exponential fits used for engineering estimates
3. API Technical Data Book – Petroleum Refining
Uses similar exponential temperature dependence for hydrocarbons
Typical C values (handbook-consistent)
Fluid Type | Typical C
Water | 1000–1300
Alcohols | 1500–2000
Hydrocarbons | 1200–3000
Heavy oils | 3000–5000
✔ Your constants fall inside published ranges
3️⃣ Specific Heat – Linear Approximation
Correlation used
Cp(T)=Cp,ref [1+a(T−Tref)]C_p(T) = C_{p,ref}\,[1 + a (T - T_{ref})]Cp​(T)=Cp,ref​[1+a(T−Tref​)]
References
1. Perry & Green – Chemical Engineers’ Handbook
Cp variation small over moderate temperature range
2. Coulson & Richardson, Vol 1
Cp often treated as constant or weak linear function
3. VDI Heat Atlas
Linear Cp approximations acceptable for HX rating
Typical a values
Liquids: 0.0001–0.0005 /°C
Aqueous solutions: lower end
✔ Your values are conservative and realistic
4️⃣ Thermal Conductivity – Weak Linear Dependence
Correlation used
k(T)=kref [1−b(T−Tref)]k(T) = k_{ref}\,[1 - b (T - T_{ref})]k(T)=kref​[1−b(T−Tref​)]
References
1. Incropera & DeWitt
Liquid thermal conductivity decreases slowly with temperature
2. VDI Heat Atlas, Section: Thermophysical Properties
Linear approximation acceptable for engineering HX calculations
3. Perry’s Handbook
k variation small compared to viscosity effects
Typical b values
Liquids: 0.0001–0.0004 /°C
Water: ~0.0002 /°C
✔ Your values align perfectly with these ranges
🧪 UTILITY FLUID DATA SOURCES
For Cooling Water, BFW, Steam, Nitrogen:
1. ASME Steam Tables
Steam density, Cp, k, μ
2. IAPWS (International Association for the Properties of Water and Steam)
Water & steam reference properties
3. Engineering Toolbox (cross-checked values)
Widely used for preliminary design
4. VDI Heat Atlas
Utilities and heat transfer fluids
References:
Property correlations and constants are based on standard chemical engineering references including Perry & Green (Chemical Engineers’ Handbook), Reid–Prausnitz–Poling (The Properties of Gases and Liquids), Coulson & Richardson, Incropera & DeWitt (Heat and Mass Transfer), VDI Heat Atlas, API Technical Data Book, ASME Steam Tables, and IAPWS formulations.
Simplified correlations are used for preliminary design and troubleshooting purposes.

## Theory behind j factors (hidden)
1 | Ideal Shell-Side Heat-Transfer j-Factor (jₕ)
jₕ is a dimensionless heat-transfer factor that represents:
Ideal heat transfer for pure cross-flow over an infinite tube bundle,
with no leakage, no bypassing, no baffle imperfections.
It is analogous to:
Nu–Re–Pr correlations in pipe flow
But developed specifically for tube bundles
jₕ is the Colburn heat-transfer factor for ideal cross-flow over a tube bundle, assuming:
No leakage
No bypassing
Uniform baffle spacing
Perfect cross-flow
👉 In reality, exchangers are not ideal, so Bell–Delaware correction factors (Jc, Jl, Jb, Js, Jr) are later applied.
But jₕ is the starting point.
The shell-side heat-transfer coefficient is calculated as:
Where:
Gs​ = shell-side mass velocity
Pr = Prandtl number
jh​ = ideal heat-transfer factor
➡️ If jₕ is wrong, everything downstream is wrong, even if all J-factors are perfect.
③ Empirical Origin of jₕ (Bell–Delaware Basis)
Developed from extensive experimental data
Based on cross-flow over tube banks
Published in:
Bell (1963)
Delaware method reports
Incorporated into TEMA / HTRI practice
The correlation depends mainly on:
Shell-side Reynolds number (Reₛ)
Tube layout (triangular, square)
Pitch ratio (Pt/Do)
Standard Bell–Delaware Correlation Form
For turbulent flow (Reₛ > 1000), jₕ is commonly expressed as:
Where:
a,b are empirical constants
Values depend on tube layout & pitch
Typical Values of Constants a and b
🔹 For Triangular layout (30° or 60°)
|  | Pitch ratio (Pt/Do) | a | b
|  | 1.25 | 0.2 | 0.6
|  | 1.33 | 0.18 | 0.62
|  | 1.5 | 0.15 | 0.65
For Square layout (90°)
|  | Pitch ratio (Pt/Do) | a | b
|  | 1.25 | 0.16 | 0.62
|  | 1.33 | 0.14 | 0.65
|  | 1.5 | 0.12 | 0.68
Engineering insight
Triangular → higher jₕ (better heat transfer)
Square → lower jₕ but easier cleaning
|  | Practical Engineering Ranges (VERY USEFUL) |  |  |  |  | Reₛ | Typical jₕ
[7 empty] | 500 | 0.01 – 0.02
[7 empty] | 1000 | 0.008 – 0.015
[7 empty] | 5000 | 0.004 – 0.008
[7 empty] | 10000 | 0.003 – 0.006
If your Excel shows jₕ outside this range, something is wrong.
Jc : Baffle Cut & Spacing Correction
What Jc physically represents
Accounts for flow through baffle window zones
Corrects the ideal cross-flow assumption
Depends mainly on:
Baffle cut (%)
Baffle spacing vs shell diameter
Jc is usually < 1.0 and typically 0.55 – 0.95
BELL–DELAWARE Jc CORRELATION (PRACTICAL FORM)
A widely used engineering approximation for Jc is:
Where:
Fw​ = window flow fraction
Depends mainly on baffle cut
Practical approximation:
Fw≈Baffle cut fraction
This is HTRI-consistent for rating/troubleshooting tools
Data validation (recommended)
Baffle Cut (%): Min 15, Max 50
Lb/Ds typical range: 0.2 – 1.0
Jl : Leakage Correction Factor
What Jl represents (plain English)
Jl accounts for shell-side leakage flows that do NOT participate in effective cross-flow heat transfer, mainly:
1. Shell-to-baffle leakage (gap between shell ID and baffle OD)
2. Tube-to-baffle leakage (clearance between tube OD and baffle hole)
These clearances are NOT calculated by the process engineer.
They are mechanical / fabrication allowances provided by the heat-exchanger vendor, usually based on TEMA standards.
These leakages reduce effective heat transfer, so:
Jl ≤ 1.0
Typical range: 0.60 – 0.95
Shell-to-Baffle Diametral Clearance
What it is
The radial gap between shell ID and baffle OD
Allows:
Fabrication tolerance
Thermal expansion
Assembly & insertion of baffles
Who decides it
Vendor / mechanical design
Based on:
|  |  |  | Shell diameter |  |  | Typical TEMA guidance (order of magnitude)
TEMA class (R, B, C)
|  |  |  | Fabrication practice |  |  | Shell ID (mm) | Typical diametral clearance (mm)
[7 empty] | < 600 | 2–3
[7 empty] | 600–1000 | 3–4
[7 empty] | 1000–1500 | 4–5
[7 empty] | > 1500 | 5–6
📌 Process engineer does not calculate this — you assume or take from datasheet.
2️⃣ Tube-to-Baffle Diametral Clearance
What it is
Clearance between tube OD and baffle hole
Needed for:
Tube insertion
Thermal expansion
Tube replacement
Who decides it
Vendor
Based on:
Tube OD
Tube material
TEMA class
Typical TEMA values
[7 empty] | Tube OD | Diametral clearance (mm)
[7 empty] | 12–19 mm | 0.4–0.8
[7 empty] | 25 mm | 0.8–1.2
[7 empty] | ≥ 38 mm | 1.0–1.5
Again: not calculated by process.
Clearances are vendor-defined mechanical inputs; process engineers only use them for performance correction, not for design.
Jb: Bundle Bypass Correction
What Jb represents (plain English)
Jb accounts for shell-side fluid bypassing the tube bundle through the gap between the tube bundle OD (Db) and the shell ID.
This bypassed flow does not effectively transfer heat, so it reduces shell-side performance.
Jb ≤ 1.0
Typical range: 0.70 – 1.00
Most impactful for large shells / small bundles
Tube Bundle Outside Diameter (Db) is NOT calculated by the process engineer.
It is a mechanical layout result provided by the HE vendor (or derived from tube count & layout during mechanical design).
As a process engineer / consultant:
You take Db from datasheet, OR
You estimate it conservatively using accepted rules only for rating / troubleshooting
Db = outside diameter of the tube bundle
Includes:
Tube OD
Tube pitch
Tube layout
Peripheral tubes
Excludes:
Shell thickness
Shell-to-bundle clearance
WHO DEFINES Db?
1️⃣ For NEW exchangers
Vendor mechanical design
Based on:
Tube count
Tube layout (triangular/square)
Pitch
TEMA class
2️⃣ For EXISTING exchangers
Mechanical datasheet
GA drawing
Vendor documentation
👉 Process engineer does not “optimize” Db.
You may estimate Db only when:
Vendor data is unavailable
You are doing rating / troubleshooting
You need Jb (bundle bypass correction)
This is acceptable if clearly documented as an estimate.
A commonly used approximation:
|  |  | Where K depends on layout: |  |  | Layout | K (typical)
[6 empty] | Triangular (30°/60°) | 0.87 | Triangular packs tubes more efficiently
[6 empty] | Square (90°) | 1 | Square is less compact
SIMPLER RULE-OF-THUMB (VERY COMMON)
Many consultants use:
[5 empty] | Layout | Rule
[5 empty] | Triangular | Db ≈ 0.90 × Ds
[5 empty] | Square | Db ≈ 0.93 × Ds
Where Ds = shell inside diameter
This is acceptable for troubleshooting tools.
Js: Unequal Baffle Spacing Correction
What Js represents (plain English)
Js corrects shell-side heat transfer when inlet and/or outlet baffle spacing differs from the central (uniform) baffle spacing.
This happens because:
Extra space near nozzles is often provided
Flow there is less effective cross-flow
Ideal correlations assume equal spacing everywhere
Js ≤ 1.0, typically 0.85 – 1.00
If inlet and outlet baffle spacing are not given, assume them equal to the central baffle spacing.
Who defines inlet/outlet spacing?
Mechanical design / vendor
Shown only on:
GA drawings
Detailed mechanical datasheets
Process engineers are not expected to invent these values.
Jr: Laminar Flow Correction
What Jr represents (plain English)
Jr corrects shell-side heat transfer when shell-side Reynolds number is low.
Bell–Delaware base correlations assume turbulent cross-flow; at low Re, heat transfer drops faster than predicted → Jr < 1.
Applies only at low Reₛ
Jr = 1.0 for turbulent flow
Typical range when applied: 0.6 – 1.0
WHEN DOES Jr APPLY? (ENGINEERING RULE)
Use the standard Bell–Delaware thresholds:
[7 empty] | Reₛ range | Action
[7 empty] | Reₛ ≥ 100 | Jr = 1.0 (no laminar penalty)
[7 empty] | 20 ≤ Reₛ < 100 | Jr applied
[7 empty] | Reₛ < 20 | Correlation unreliable → warn user
Bell–Delaware Pressure-Drop (ΔP) — STRUCTURE
ENGINEERING FORM (BELL–DELAWARE PRACTICAL MODEL
Shell-side pressure drop is composed of four physical components:
PHYSICAL DECOMPOSITION (FUNDAMENTAL)
[5 empty] | Where: |  |  |  |  | What Bell–Delaware did (THIS IS THE KEY)
[5 empty] | Term | Meaning |  |  |  |  | Bell and Delaware researchers observed:
[5 empty] | ΔP_cf | Cross-flow pressure drop between baffles |  |  |  |  | Leakage and bypass flows do not add pressure drop —
[5 empty] | ΔP_w | Window zone (baffle cut) pressure drop | [5 empty] | they reduce the effective resistance of the main crossflow.
[5 empty] | ΔP_leak | Leakage flow pressure drop | [5 empty] | So instead of:
[5 empty] | ΔP_bypass | Bundle bypass pressure drop | [6 empty] | adding ΔP_leak and ΔP_bypass
|  |  | ✔ This is conceptually exact | [9 empty] | they embedded their effects as reduction factors:
✔ Used in derivations and research
|  |  | ❌ Not practical for engineering tools (too many unknowns) | [10 empty] | Factor | Represents
|  | Bell–Delaware applies correction factors, just like heat transfer. | [11 empty] | Rl​ | Effect of leakage streams
[14 empty] | Rb​ | Effect of bypass streams
| IDEAL CROSS-FLOW PRESSURE DROP (ΔP_cf) | [12 empty] | These reduce the base pressure drop, rather than adding to it.
This is the dominant term.
C ≈ 2.5 (triangular & square – acceptable for rating)
WINDOW ZONE PRESSURE DROP (ΔP_w)